붙임 2. 과업지시서 (제품 제조 사양서)

1. Turbo Fan System

I.D Fan	Type	Sirocco Fan
	Material	Steel
	Power	220v3Ø
	Air Volume	700㎥/min
	Motor	11.25kw
	Static Pressure	50mmAq
	Qt'y	1 Set`
In - Let Fan	Type	Sirocco Fan
	Power	220v3Ø
	Air Volume	350㎥/min
	Motor	7.5kw
	Static Pressure	50mmAq
	Qt'y	2 Set`
Purge Fan	Type	Turbo Fan
	Power	220v1Ø
	Air Volume	10㎥/min
	Motor	0.75kw
	Static Pressure	250mmAq
	Qt'y	2 Set`
Ass'y	Purge Heater	3kw x 1Ø x 4ea
	Manual Damper	750Ø x 2ea
	Manual Damper	1000Ø x 1ea
	Canvas	1000Ø x 1ea
	Duct & Stack	750/1000Ø
1차 Collecting parts	Size	3700W*2700H*1200L
	Material	SUS + AL panel
	Manhole	Steel 6t 700*500 6t 5ea
	Discharge Electrode	STS3040.3t3000*30 300ea
	Spring	Steel200*9Ø1200ea
	Discharge Electrode frame	Steel 5t 800*250*3500 2ea
	Discharge plate	Aluminium1000*27004t 38ea
	Qt'y	1 Set

2차 Collecting parts	Size	3700W*2700H*1200L
	Material	SUS + AL panel
	Manhole	Steel 6t 700*500 6t 5ea
	Discharge Electrode	STS3040.3t3000*30 300ea
	Spring	Steel200*9Ø1200ea
	Discharge Electrode frame	Steel 5t 800*250*3500 2ea
	Discharge plate	Aluminium1000*27004t 38ea
	Qt'y	1 Set

2. Spray Pump System

Pump	Model	HES 100-200
	Type	Single Stage Volute Pump
	Power	220V3Φ
	Motor	11kw
	유량	2.2㎥/min
	Qt'y	2
Nozzle	Type	FLAT
	Material	BRASS
	Nozzle No 150	3/4"
	Water Flow	60 l/min
	Injection Angle	110°
	Pressure	0.3kg/㎠
	Qt'y	36
Water tank	Material	SS 41
	Size	2000W*3000L*1200H
	Pump flange	Suc1250A-Dis100A
	Over flow	65A
	Drain	65A
	City water	15A
	PUmp inlet	125A
Mist separator	Type	Lamelar
	Size	2000 * 2500 * 300t
	Material	SS41
	Face velocity	2.5m/s
	Efficiency	5μ이상95%
	Qt'y	2
Auto V/V	Model	HQ-015
	Type	ELECTRIC ACTUATOR (ON/OFF)
	Power	220V1Φ
	Qt'y	3

Oil Skimer	Model	DHOS-B8
	Type	BELT
	Power	220V3Φ
	Motor	Gearedmotor
	Ratio	1/100
	RPM	18
	Qt'y	1
Ass'y	SPP PIPE	125A/100A외
	Flang/Tee/Elbow	125A/100A외
	Ball V/V	125A/100A외
	Canvas	1000Ø x 1ea
	Duct & Stack	750/1000Ø

3. MCC Electric System

TYPE		Pulse
T/R	BODY	1500*1000*670 steel 3.2t
	DC Output Power H/V Bushing	VERTICALMOUNTING(200kVBIL) BL200kv
	Control method	SCR에의한위상각제어
	DCOutputPower	39kV-RMS, 27.5kVA
		89Am/28kvrms/500ma
	% IMPEDANCE	30%
	Cooling Type	유입자냉식
	Ambient temperature	40° 이하
TYPE		옥외 자립형
Control panel	BODY	Plate steel 2.3t
		Door steel 3.2t
	H.V Control Unit	AVC-2000
	사양	고압발생기40kw
		Fan 7.5kw x 2대, 11.25kw x 1대
		Pump motor 11kw x 2대
		Purgefan0.75kwx4대
		Purge heater 3.0kw x 4대
Upper Insulator	Body	1600*3700*2000
	Material	Steel
	Manhole	Steel 6t 700*700 1ea
	Insulator box	Steel6t300Ø4ea
	Support insulator	Ceramic 안테나(대) 4ea
Lower Insulator	Body	1600*3700*2000
	Material	Steel
	Manhole	Steel 6t 700*700
	Insulator box	Steel 6t 400*400
	Support insulator	Ceramic 안테나(대) 4ea

Ass'y	전압계	0~600V
	전류계	0~75A
	전력계	전산 TYPE
	전선	CV 16외
	전선관	28C 외